Chapter 3

# Uncertainty and Related Issues

## 3.1.  Uncertainty

All reliability parameters of the Safety Amplifier quantify, in one way or another, the underlying failure process that is random in nature, and therefore they all have associated uncertainties. Each uncertainty depends on the shape of the random variable’s distribution function and is numerically expressed as the distribution’s second moment. If the shape of the distribution function is more complex we may as well need to include higher moments to appropriately present other characteristics, such as skew, for example. Note that these moments are random variables themselves or more precisely statistics, which is why we may talk about uncertainties circularly.

### Origins of Uncertainty

Uncertainties of the resulting Safety Amp reliability parameters have several origins. We may divide these origins into two main groups:

Group 1. Uncertainties due to the lack of knowledge, including

- Insufficient statistical data (censoring insufficiency)

- Uncertainties due to the imperfect modeling (assuming independent events, using exponential distributions, fault tree technique for modeling, etc.)

- Uncertainties due to numerical approximations (numerical round-off, maximum cut set order truncation, etc.)

- Uncertainties due to other approximations and assumptions

Group 2. Uncertainties due to the stochastic nature of the failure process itself,

including

- Uncertainties caused by differences from one component to another

- Uncertainties due to different maintenance policies

- Uncertainties due to different operational demands

- Uncertainties caused by different environmental conditions

This division is characterized by the notion that the uncertainties of the first group are the only one that can be reduced without physically affecting the equipment or its surroundings. Therefore, the uncertainties of the second group at the time of analysis can be calculated but cannot be changed.

### 3.1.2.  Models with Independent Second Moment

Each uncertainty value will be associated to either normal or lognormal distribution. The normal distribution is given by

(3.1)

where  denotes the mean value, and  denotes the standard deviation, i.e. uncertainty. Lognormal distribution is suitable for random variables that can only have values grater

or equal to zero. The lognormal distribution is given by

(3.2)

where the mean and standard deviation are respectively given by

(3.3)

Instead of being associated to the standard deviation, uncertainty of log-normal distribution is commonly associated to the error factor given by

(3.4)

Note that uncertainty has practical meaning only when expressed in certain units. Uncertainty of three dollars when the mean is two dollars means more than uncertainty of five dollars when the mean is one thousand dollars. To compensate for this, we would express uncertainty in terms of a unit without dimension. This dimensionless unit, defined as =(/) is named the coefficient of variation.

## Minimal Cut Set Method

### 3.2.1. Minimal Cut Set Approximation

When the number of branches in the reliability graph (see Figure [3-1]) becomes large, an approximate method based on the notions of path set and cut set is used to calculate the system reliability. A path set is a set of branches that forms a connection between input and output when traversed in the direction of the arrows. A minimal path set is a path set containing branches such that no node is traversed more than once in tracing out a path set. Similarly, a cut set is a set of branches that interrupts all connections between input and output if removed from the graph. A minimal cut set is a cut set that does not contain any other cut set except itself.

For example, some path sets of the graph in Figure [3-1] are: {1,3,8}, {1,3,7,6}, {1,3,7,5,8}, {1,3,7,9,2,6}, {1,3,7,9,2,5,8}, {1,3,7,9,8}, {1,4}, {2,5,8}, {2,5,7,6}, {2,5,7,9,1,3,8}, {2,5,7,9,1,4}, {2,5,7,9,1,3,6}, {2,6}. Minimal path sets are: {1,3,8}, {1,3,7,6}, {1,4}, {2,5,8}, {2,6}. Minimal cut sets are: {1,2}, {1,5,6}, {1,6,8}, {3,4,2}, {3,4,5,6}, {8,4,2}, {8,4,6}.

3

2

6

8

4

5

1

output

input

7

9

Figure 3-1. Reliability graph

If Sj denotes that all subsystems in the j-th minimal path set survived for a length of time t, then the system reliability is given by

(3.5)

or

(3.6)

A good approximation to R(t) in the low reliability region is given by assuming that events Sj are mutually exclusive, so that the second term at the right-hand side becomes zero. This gives the following upper bound inequality

(3.7)

Similarly, if Fj denotes that all subsystems in the j-th minimal cut set fail prior to time t, than the exact system reliability is given by

(3.8)

Using the rare event approximation once again, we can find the inequality for the lower bound suitable for the high reliability region

(3.9)

Note that rare event approximation utilizes the fact that if the events are rare and independent, then, as an approximation, they can be considered being mutually exclusive.

It is important to realize that when the minimal cut set method is used, the resulting parameters are conservative in mean. For example, the calculated unavailability would be overestimated, meaning that the true value of the unavailability is likely to be shifted to the left on a real axis. As the true values are not known, we can only do the uncertainty analysis using the calculated values bearing in mind, as we explained, that these values are systematically biased. Nevertheless, as we are about to show, the unavailability bias caused by minimal cut set approximation is rather small.

### The Bias

As it was shown in the previous section, a cut set method yields the upper bound of system unreliability and is close yet conservative approximation in cases when unreliabilities of the components are sufficiently small. We can find the upper bound of the bias of the minimal cut set approximation by using the “second term expansion” of the unreliability expressed in a cut set form. If Fj (j=1,…,n) denotes the event that all components in the j-th minimal cut set fail prior to time t, then the exact system unreliability is given by

(3.10)

Therefore,

(3.11)

and since j  0, then

(3.12)

and also

(3.13)

The right hand sides of the above equations represent respectively that the upper bound of “true” reliability is the minimal cut set approximation, and that the upper bound of the bias of this approximation is 2. Note that, consequently, (1-2) forms the lower bound for U(t).

Since the event Fj associated with the j-th cut set represents an intersection of component failure events, in the case where component failures are considered to be mutually exclusive events the probabilities of the cut set events will all be equal to zero. In minimal cut set approximation we therefore assume that the component failures are only statistically independent, but that the cut set events are mutually exclusive. This assumption is reasonable since cut set failure probabilities are many times smaller than component failure probabilities (apparently, cut set failures are less frequent than system failures). This results in 2=0 which gives the minimal cut set approximation of U(t)=1. Following this line of thought, we can “shift” the cut sets in the direction from more stringent to less stringent condition in the same way that we did for component failure events. Thus by using less stringent (yet more realistic) assumption that the cut set events are not mutually exclusive but only pair-wise independent, the following inequality can be derived

(3.14)

Hence, the bias of the minimal cut set unreliability approximation 1 is found to be smaller than the approximation value itself squared over two, i.e.

(3.15)

From the given discussion it follows that a close approximation to the system unreliability, although not necessary conservative, is given by following exponential expression

(3.16)

where 1 denotes a minimal cut set approximation. This expression has identical form as the expression for the reliability of a single memoryless component.

For the system undergoing repair, evidently, the identical set of expressions can be derived for the system’s unavailability.

## Confidence

### 3.3.1.  Interval Estimation

After quantifying the uncertainties of estimated reliability parameters we can use these uncertainties, i.e. standard deviations, to express our confidence that a particular reliability parameter is enclosed in some interval of real-valued numbers. For positive random variable Y the following Cantelli inequalities are in effect

(3.17)

(3.17)

where “” denotes the mathematical expectation of X or ‘mean’, while “” denotes its standard deviation.

### How does the FaultTree+ Calculate the Confidence?

FaultTree+ uses Monte Carlo simulation in order to calculate the level of confidence of the gates and consequence parameters. Event unavailabilities and event frequencies are determined by random sampling from the specified uncertainty distribution for event data model parameters. As we already mentioned these distributions are either Normal or Lognormal, which will largely be determined by availability of the particular failure data model for the basic events. Maximum number of simulations is set to 20,000.

## Are we too conservative?

Applying Log-normal distribution is seemingly justified in cases when the random variable is restricted to the positive half of the real axis. Despite the fact that it was adopted in WASH-1400, in many cases of interest Log-normal distribution does not provide adequate results. In fact, both Normal and Log-normal distributions have tails that are infinitely long. From practical experience we know that the real values are often bounded. However, cutting off the tail would introduce immense analytical difficulties. Yet, we can miscalculate the reliability significantly by including the tail that is “too thick”. Hence, in order to overcome the possible error introduced by the thick tail of Log-normal distribution we may use another distribution that doesn’t have a tail. A good candidate is a Log-uniform distribution. Because Log-uniform distribution is “flat” or “uninformative” (this was first noticed by Jeffreys in his celebrated work, see Jeffreys [1948]), in many cases it gives better results than Normal or Log-normal distribution. Still, the rationale behind the meaningfulness of Log-normal distribution is rather weak. That is why we will not use it for purposes other than to estimate the possible error caused by allowing finite probabilities to be assigned to events outside any reasonably chosen time-intervals. Although Jeffreys’ work in ocean waves represents the foundation of the modern Bayesian statistics, until today it has remained non-compliant with the classical inferential techniques advocated by Fisher, Neyman, Pearson, and others from the “English” school, and therefore has not been officially accepted nor recommended by regulatory agencies.

## Sensitivity

The system sensitivity S of the reliability parameter X to the characteristic system failure rate  is given by

(3.18)

The MTTF sensitivity of the system composed of two parallel units without repair is equal to the sensitivity of the single unit, but is smaller than the sensitivity of the system with repair. This is the price we pay for increasing the system’s reliability in the later case. The above two cases yield:

(3.19)

Obviously, 10% change in the failure rate would result in 10% change in MTTF1 but in 20% change in MTTF2. According to Equation (3.19), the sensitivity of the two parallel units with repair, S2, compared to the sensitivity of the identical two parallel units without repair, S1, is

(3.20)

This result means that we have to find more accurate failure rates for basic events in order to meet the same confidence bounds of the resulting system parameters – reliability, MTTF, etc. – compared to the case of a single unit or two parallel units without repair.

Event unavailabilities and failure frequencies in a FaultTree+ program are varied above and below the normal values automatically by the specified percentage, which gives the sensitivity of the gates that may, in return, alter the values in the table of event tree consequences.

## Importance

### Deterministic view

Traditional reliability theory requires that, in order for any component j to become a part of the structure function  of the coherent system, it must be relevant, namely the following condition must not be satisfied for all  x=(x1,…,xj-1,xj+1,…,xn)=(xj-,xj+)

(3.21)

##### Here, for brevity, vector xj- stands for (x1,…,xj-1) component, xj+ stands for (xj+1,…,xn) component, and x =(xj-,xj+). In other words, the definition of the coherent system merely states that for each component j there is at least one state x of the rest of the system that satisfies the condition (1j,x)  (0j,x). From this point of view, all relevant components are “equally” relevant, because the above definition does not specify how many different states ‘x’ there are. This may lead us to a conclusion that not all of the relevant components are equally important. For any component j and state x only one of the following two cases may happen

(3.22)

Since there are 2n-1 different states x (it should be understood that x is related to j, indexes are omitted for brevity, i.e xxj) we may define the structural importance of component j as a measure

(3.23)

This would correspond to a stochastic measure in the case of complete lack of information, although this measure is slightly biased due to somewhat “clumsy” definition of the structure function. In addition to the lattice generated by , structural importance canonically generates a relation of order “” or lattice  in the set of state vectors y as

(3.24)

### Stochastic view

A simple reliability importance can be defined as a measure of the variation of the system’s reliability (availability) when the component’s failure probability is being varied. Hence,

(3.25)

In case of independent events

(3.26)

and therefore

(3.27)

As you may recall, ( j , Xj)  (X1 ,…, Xj-1 ,  j , Xj+1 ,…, Xn).

The rate at which system reliability (availability) is perturbed by any “other” variable, such as time for example, is a weighted combination of the rates at which component reliabilities (availabilities) change, where the weights are the reliability importance numbers. This can be obtained by using the chain rule of differentiation. For example

(3.28)

### Other importance measures

Importance measures that will be calculated for the Safety Amplifier are (see “A Technical Document Issued by the Isograph Ltd” [1995]):

- Fussell-Vesely Importance,

or the event’s contribution to the system unavailability:

- Birnbaum Importance,

or the sensitivity of system unavailability with respect to changes in the event’s unavailability:

- Barlow-Proschan Importance,

or the probability that the system fails because a critical cut set containing the event fails, with the event failing last:

### These importance measures will be calculated and presented as a part of the results of the Safety Amplifier fault tree analysis. It will be shown that the common cause failures have the highest importance measures, followed by resistor R49, which represents the bottleneck in the signal flow. An importance measure measures the sensitivity of the system’s unavailability with respect to the failure probability of a certain component. These probabilities are not fully known. It is therefore important that the components with high importance measures have small uncertainties of their failure rates. Unfortunately, high uncertainty is the main characteristic of the common cause failures, which, as we already concluded, also have the highest importance measures in the Safety Amplifier.