STATISTICAL ESTIMATION OF THE UNAVAILABILITY

OF THE MNR SAFETY AMPLIFIER

By

IMRE VENCEL

A Thesis

Submitted to the School of Graduate Studies

in Partial Fulfillment of the Requirements

for the Degree

Master of Engineering

McMaster University

© Copyright by Imre Vencel, May 2000

# MASTER OF ENGINEERING (1999)				McMaster University

(Engineering Physics)							     Hamilton, Ontario

TITLE: Statistical Estimation of the Unavailability of the MNR Safety Amplifier

AUTHOR: Imre Vencel, B.Sc. (Belgrade University)

SUPERVISOR: Professor Wm. J. Garland

NUMBER OF PAGES: xii, 161

ABSTRACT

Unavailability of the McMaster Nuclear Reactor (MNR) Safety Amplifier is calculated and showed to be within acceptable limits. Treated as a system of moderate complexity, the MNR Safety Amplifier reliability parameters are studied in detail utilizing a fault tree technique. This technique is recommended by IAEA and widely adopted in nuclear engineering as a main route for performing probabilistic risk assessment. A fault tree is developed and reliability parameters are calculated using a commercial software application FaultTree+™. Component failure data were collected from IAEA technical documents or other reliable sources when available. Uncertainty and importance analyses have been performed. In addition to the failure rates obtained from external documents, the Safety Amplifier checkout procedures were incorporated into the effective repair rates, thus forming the complete model for the basic events of the fault tree. The cut-set analysis methodology was utilized in order to assure that the final results would be reasonably biased, i.e. conservative enough. For the same reason, only the reliability data with established bounds of confidence were used. The resulting reliability parameters indicate that the failures of the Safety Amplifier caused by external means may be much more frequent than those caused by random failures of the individual components.

™ FaultTree+ is a trademark of Isograph Ltd.

ACKNOWLEDGEMENTS

Many people have helped me in one way or another in the preparation of this thesis. I wish to thank my supervisor, William J. Garland, for his much-valued critical readings and constant support during the writing of this thesis. My thanks go also to my colleges Simon Day, John Kennedy, and Robert Pasuta, for their comments and constructive suggestions. Special thanks go to my parents, without whose continued encouragement and support this work would have never been completed.

I want to express my appreciation for the financial support provided by the Engineering Physics Department and School of Graduate Studies at McMaster University. Also, I am grateful for the financial support provided by the Ontario Ministry of Education and Training Student Opportunity Trust Funds Program. This financial support came from the funds established by family, friends and colleagues of Robert John Morris.

Contents

Introduction	……………………………………………………………………………..1

Chapter 1. MNR Safety Amplifier Decomposition

1.1. Introduction to Fault Tree Analysis   ………………………………………10 1.2. Uncertainty Propagation in a Fault Tree  ……..……………………………12 1.3. Modular Decomposition. Threads   …………..…………………………….15 1.4. Repairable Systems with Supervision   ..……..…………………………….24 1.5. Subsystems and the Unit Prototype  …………..……………………………28 1.6. I/O Modes  ……………………………………..…………………………...33 1.7. Insufficiencies of the Traditional Reliability Theory  ……..……………….34 1.8. Reliability Functions of the Multi-input Systems  .…………………………38

  - Initiating Events that may lead to Improbable Failures

of the Safety Amplifier   ……………………………………………………41

Chapter 2. MNR Safety Amplifier Subsystem Analysis

2.1. UIC Subsystem ………………………...……..…………………………….42 2.2. SDA Subsystem  ……………………….……..…………………………….44 2.3. SRY Subsystem   ……………………….……..……………………………51 2.4. Slow Scram Subsystem Interdependencies  .…….………………………….55

2.4.1. Calculation of Availabilities by Event Space

Decomposition Method  …………………………………………..55

2.4.2. Calculation of Availabilities by Minimal Cut Set

Approximation Method  …………………………………………..59

2.5. Divider  ….……………………...…………………………………………..62

2.6. FSP Subsystem  ………………...…………………………………………..66

## 2.7. Implementation of the Dual Filament Burn-Out Feature

## that has Acceptably Low Resulting Unavailability   ……………………….68

## 2.8. Fast vs. Slow Scram: R49 Failure Case  .….……………….………………70

Chapter 3. Uncertainty and Related Issues

3.1. Uncertainty     ..…..…………………………..……………………….…….78

3.1.1. Origins of Uncertainty     ……………………………..…………..78 3.1.2. Models with Independent Second Moment       …………………..80

3.2. Minimal Cut Set Method   …………….……………………………………81		3.2.1. Minimal Cut Set Approximation    …………………………….…81   	3.2.2. The Bias    ……...…………………………………………………83

3.3. Confidence     .………………………………………………………………86

3.3.1. Interval estimation    …………………………………………………86

3.3.2. How does the FaultTree+ Calculate the Confidence?      ……………87

3.4. Are we too conservative?     ………………………………………………..87

3.5. Sensitivity      ...……………………………………………………………..88

3.6. Importance  .....……………………………………………………………...90

3.6.1. Deterministic view      ...……………………………………………...90

3.6.2. Stochastic view       .…….……………………………………………91

3.6.3. Other Importance Measures    .......…………………………………..92

Chapter 4. Common Cause Failures

4.1. Power Supply  ..………………………..……………………….…………..96

4.2. Operator Error   ………………………..……………………….…………..97

4.3. Failure on Demand   …………………..……………………….……….…..98

4.4. External Common Cause Failures  ...………………………….…………..102

4.5. Beta Factor Method ……………………..……………………….………..103

Chapter 5. Results of the Fault Tree Analysis

5.1. Component Reliability Data   ......………………………………………….105

5.1.1. Conversion Factors ......…...…………………………………….105 5.1.2. Reliability Database  ..……………………………………..….…107

5.2. Basic Event Model Construction   ………....……………………………...108

5.3. List of Results   ..……….…..…...…………………………………………109

Conclusion  ……………………………………………………………………………152

Appendix 1: Principle of Total Probability  ………………………………………...156

Appendix 2: An Example of an Incoherent System  ………………………………..158

List of References   ……………………………………………………………………160

List of Figures

Figure 1-1. System in the standby parallel mode  ...……………………………………..11 Figure 1-2. Fault Tree Symbols  ...………………………………………………………12  Figure 1-3. The comparison between absolute and relative sizes of intersections

for various event-frequency pairs …………………………………………13 Figure 1-4. The connectivity between the UIC chambers and the Safety Amplifier ……17 Figure 1-5. Fault trees of the Safety Amplifier   ………………………………………..19 Figure 1-6. MNR Safety Amplifier Electronic Circuit   ………………………………..21 Figure 1-7. MNR Safety Amplifier Success Signal Propagation Chart    ………………22  Figure 1-8. MNR Safety Amplifier Success Signal Propagation Chart,

Matrix Form   …...……………………………………………..………………23 Figure 1-9. Timeline Diagram of a System with Two Active Parallel Units    …………25 Figure 1-10. Typical Unit of the Safety Amplifier …………………………………….28 Figure 1-11. Signal Flow and Information Channels   ………………………………..30 Figure 1-12. Symbol Denoting the Typical Unit in Signal Flow Charts   ……………..32 Figure 1-13. Multiple Inputs Enclosed in a Supergraph   ……………………………..40 Figure 2-1. UIC-1 Unit  ..……………………………………………………………….43 Figure 2-2. SDA-1 Unit .……………………………………………………………….45 Figure 2-3. Operating U-I Characteristics with CAS on the Interface  ....…………….49 Figure 2-4. Parallel Thread Designed as: Dormant Closed Line (DCL, left),

and Dormant Opened Line (DOL, right)…   .....……………………………..51 Figure 2-5. SRY-1 Unit  .…………………….………………………………………..53 Figure 2-6. SSS-1 Reliability Graph and a Sample Cut Set …….………………...61 Figure 2-7. DIV Subsystem   ..……………………………………….………………..62 Figure 2-8. Predicted Failure Rates of Fixed Composition Resistors ….……………......63

Figure 2-9. V3 (or FSP-1) Unit  ….....………………….………………………………..67

#### Figure 2-10. Figure 2-10. Equivalent Single Filament Circuit for

#### Dual Filament Burn-out   ………………………………………………….70 Figure 3-1. Reliability Graph    ....…...……………………………………………...……82 Figure 5-1. Top Portion of the Safety Amplifier Fault Tree (UIC Input) ……….……113 Figure 5-2. Top Portion of the Safety Amplifier Fault Tree (Log-N Input) .…………..114 Figure 5-3. FSP Subsystem Fault Tree Branch: 2.5 Out of 4 Logic  .…………………115 Figure 5-4. FSP Subsystem Fault Tree Branch (Simplified)  …….….………………116 Figure 5-5. FST Subsystem Fault Tree Branch  ..…...……………..…………………117 Figure 5-6. SST Subsystem Fault Tree Branch (Collapsed) ………………………….118 Figure 5-7. SST Subsystem Fault Tree Branch (Expanded)  …….………………….119 Figure 5-8. UIC Subsystem Fault Tree Branch  ...…………………………………….120 Figure 5-9. Safety Amplifier Fault Tree (UIC Input, Expanded)   …….………………121

List of Tables

Table 1-1. Components of the Typical Unit That Correspond to

Different Modular Units   ……………………...……………………………31 Table 2-1. Electronic Systems Reliability  .……………………………………………..64

Table 5-1. Safety Amplifier Root Event Summary .…………………………………...110

Table 5-2. Safety Amplifier Root Importance Ranking  ...…………………………….111 Table 5-3. Minimal Cut Sets with Highest Unavailabilities   ....……………………….111 Table 5-4. Gate Summary   …………………………………....………………………122